**INTERNATIONAL CENTRE FOR GENETIC ENGINEERING AND BIOTECHNOLOGY**

JNU CAMPUS, ARUNA ASAF ALI MARG,

NEW DELHI 110067

NOTICE INVITING TENDER

Sealed bids are invited from reputed and experienced vendors for undertaking the following work

Name of the Work: **Supply, Installation, testing and commissioning of AHU (Qty 07) and related works under buy back of existing AHU (Qty 07) including dismantling.**

Schedule:

1. Date of bid submission and time: **12th August, 2019 and 3:00 PM**
2. Date of technical bid opening and time: **12th August, 2019 and 4:00 PM**
3. Date of Financial bid opening: **Will be intimated to technically qualified bidders**
4. Place of Financial bid opening: **Conference room ICGEB, New Delhi**

The Scope of work and the tender document are appended below can be down loaded from our website and access the links on to <http://www.icgeb.res.in/ndinfo.htm> Interest and eligible contractors are requested to submit the bid complete in all respect along with a tender fee of **Rs.500.00 (Non- refundable)** and EMD of **Rs. 50,000/-** Bids received without the tender fee and EMD will be summarily rejected.

ICGEB reserves the right of outright rejection of all the bid received without assigning any reason. The decision of the institute will be final and binding on all the bidders. In case of cancellation of tender for any reason, the bids will be retained with ICGEB and will not be returned back to the contractor, however EMD will be returned.

**Instructions for Bid submission**

**Technical bid should contain proof of the following:**

1. The Bidder should be Reputed contractor/Supplier and must have executed at-least one similar work of

 Rs 20Lacs, or Two similar work of Rs 12.5 Lacs each or 03 works of Rs 10 Lacs each -in Govt./ PSU/Autonomous bodies, International institutions or Reputed private sector.

 (b) Bidder should have its firm/ and or office in Delhi-NCR.

 (c) Copies of documents for eligibility criteria must be submitted along with Draft of EMD **in technical bid**.

 (d) The sealed price bids should be submitted in separate sealed envelope super scribed accordingly on the envelope and dropped in the tender box at the reception of ICGEB, New Delhi. Bids received after the schedule time & date will not be entertained or returned

(e) Copy oftender document page numbered, signed and stamped on each page by the authorized signatory

(f) Both “Technical” and “Price” bid should be in separate envelops and then put in to one common envelope, super scribing the name of the work and tender opening date etc.

**Financial bid** envelop must contain duly filled, signed and stamped financial bid. The both envelops should be super-scribed clearly with Name of work and NIT No 05/2019, providing name(s)and postal address of the Bidder with Phone/ Mobile/ Fax numbers and e-mail address if any.

The offer shall remain open for at least 60 days. Earnest Money Deposit (EMD) amounting to Rs. 50,000/-shall be accepted only in the form of Demand Draft drawn in favour of the ICGEB, New Delhi, and payable at New Delhi. EMD and tender fee must be enclosed with technical bid failing which, bid will summarily be rejected.

 **SCOPE OF WORK**

|  |  |  |
| --- | --- | --- |
| **S. No.** | **Item Description** | **Qty** |
| 1 | Supply,installation,testing and commissioning of 16700 CFM at 50mm wc factory fabricated double skin chilled water air handling unit horizontal type (floor model)fabricated out of extruded aluminium section with 0.6 mm preplasticized / pre coated galvanized steel sheet outside & 0.6 mm plain galvanized steel sheet inside with DIDW forward curved blower, blower section and blower motor TEFC type suitable for operation on 415 volts +- 10 %, 50 Hz +- 5 % AC supply , 6 Row deep chilled water cooling coil made of Aluminium finned copper tube (tube thickness 0.5mm) with coil section, pre filter section with non woven synthetic media of 10 micron particle size with an efficiency of 90 %, polished stainless steel drain pan made out of at least 20 G thick sheet duly insulated, complete with motor and belt drive package etc. The AHU panels shall be insulated with 23 mm thick & 38 kg/cum density PU foam. The complete AHU shall conform to standard specifications. The face velocity across cooling coil shall be limited to 150 MPM max. The capacity of Air Handling unit shall be as mentioned hereunder. (MAKE ZECO/EDGETECH/WAVES/) |   |
| a | 16700 CFM at 50 mm WC, | 1 |
| b | 10700 CFM at 50 mm WC | 1 |
| c | 8700 CFM at 50 mm WC, | 2nos |
| d | 5700 CFM at 50 mm WC | 2 nos |
| 2 | Supply,installation,testing and commissioning of 6000 CFM at 50mm wc factory fabricated double skin chilled water air handling unit horizontal type (floor model)fabricated out of extruded aluminium section with 0.6 mm preplasticized / pre coated galvanized steel sheet outside & 0.6 mm plain galvanized steel sheet inside with DIDW forward curved blower, blower section and blower motor TEFC type suitable for operation on 415 volts +- 10 %, 50 Hz +- 5 % AC supply , 8 Row deep chilled water cooling coil made of Aluminium finned copper tube (tube thickness 0.5mm) with coil section, pre filter section with non woven synthetic media of 10 micron particle size with an efficiency of 90 %, polished stainless steel drain pan made out of at least 20 G thick sheet duly insulated, complete with motor and belt drive package etc. The AHU panels shall be insulated with 23 mm thick & 38 kg/cum density PU foam. The complete AHU shall conform to standard specifications. The face velocity across cooling coil shall be limited to 150 MPM max. The capacity of Air Handling unit shall be as mentioned hereunder. (MAKE ZECO/EDGETECH/WAVES/) | 01 no |
| 3 | Providing and fixing butterfly valves of following size duly insulated complete as required. (Make: Audco/ Honeywell/Advance) |   |
| a | 80mm  | 2 nos |
| b | 65 mm  | 06 nos |
| 4 | Supply ,installation,testing and commissioning of Y type pipeline strainers of following size duly insulated and necessary fittings complete as required(make;Advance,Zoloto) . |  |
| a | 80 mm | 01 nos |
| b | 65 mm | 05 nos |
| 5 | Providing and fixing balancing valves of following size duly insulated complete as reqd.(make;Advance/sant/zoloto) |   |
| a | 80mm  | 1 |
| b | 50 mm  | 5 nos |
| 6 | Supply ,installation,testing and commissioning of 65 mm size c class MS pipe with insulation with necessary fittings and insulating chilled pipeline using "TF" grade expanded polystyrene moulded pipe sections of density not less than 20kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) covered with a layer of 120 grams/sq m polythene sheet (vapour barrier) & finally applying 0.63mm Aluminium sheet cladding complete as required. ( Pipe make JINDAL,TATA / EPS insulation make: Beardsell ) | 30 meter |
| 7 | Supply, installation, testing & commissioning of 2 way modulating valve, linier type,thermostat,temperature controller, interconnecting wires,flange,nut,bolt,welding complete as required (Make, SIEMENS,DANFOSS). The size of modulating valve shall be as mentioned hereunder.  |   |
| a | 65 mm  | 02 nos |
| b | 50 mm  | 19 nos |
| c | 32 mm | 10 nos |
| 8 | Supply ,installation,testing and commissioning of duct connect new AHU to existing ducting used 22 gauge GSS in class v111,as per IS 655 and,thermal insulation of supply air duct with crosslinked closed cell performed section of polyethylene(FR) insulation of 13 mmthick laminated with aluminium matalised polyester foil .  | 20 sq met |
| 9 | Supply, installation, testing and commissioning of Mercury filled **'V' form thermometer** with SS/browns body, thermo well as required(Make H GURU,JASPIN ). | 14 nos |
| 10 | Providing and fixing of pressure gauge 0-10 kg/sq cm,100 mm dial size,with ss syphon,heavy duty isolating ball valves ,1/2 inch ball valve for AHU water air purging complete as required.(Make H GURU,JASPIN ).). | 14 nos |
| 11 | Providing and fixing good quality fire retardent flexible canvass connections complete as required | 07nos |
| 12 | Modification of ducting arrangement near AO's room to block the existing duct connection from the existing AHU (this AHU 2000 cfm presently installed in the AO's secretariate room shall be dismantled and removed permanently, AHU room separation two side 04 inch brick wall removing repairing and painting as required ) and to connect the main duct running in the corridor with the existing ducting to feed the AO's room as required. | 01 job |
| 13 | Buy back of dismantled AHU materials. | 07 nos |

 **(TECHNICAL BID)**

**Eligibility Criteria**

1 Name of the Agency:

2. Office Address and Tel. Nos. Email ID:

3.Registration details (with documentary evidence)

4. PAN No. (with documentary evidence)

5. Annual turnover for last three years supported with documentary evidence.

6. Experience (last three years) (copies of work orders and completion certificates if fully executed)

7. Tender Fee

8. Earnest Money Deposit

**GENERAL TERMS AND CONDITIONS**

Name of the Work: **Supply, Installation , testing and commissioning of AHU(Qty 07) and related works under buy back of existing AHU(Qty 07) including dismantling.**

1) The Work shall be done as per schedule of items, specification terms and conditions and instruction of Engineer-in-charge on as and when required basis.

2) Time limit 30 days from the date of the order issued.

3) The rates shall be inclusive of cartage/ loading unloading or any other expenses. GST should be clearly shown separately. Rate must be valid and firm for a period of six months from the date of award of contract/Letter.

4) No Extra charge or any escalation charge will be paid by company.

5) Inferior and Poor quality material will be rejected and work order may be cancelled.

6) The contractor will have to undertake responsibility of accidents etc. for his persons working on line and same will be on stamped paper of Rs.50/100 or the appropriate value (if revised by Govt) The cost of stamp will be borne by the contractor.

7) Before quoting, the contractor is advised to inspect the site of work and shall fully acquaint himself about the conditions and scope of work with regard to accessibility of site required for the satisfactory execution of work. No claim whatsoever shall be entertained by the deptt. on this account.

8) Contractor is to follow relevant Indian standards fire, electricity, safety and building rules.

9) The Contractor shall clean the site after completion of work in all. Any dismantled material shall be stacked in designated place as instructed by the Engineer-in-charge.

10) Charges for **scaffolding or jhula** if any, will considered included in the quoted rates and no extra amount will be paid on this account.

11) Measurement shall be taken jointly by the Engineer-in-Charge or his authorized representative and by the contractor or his authorized representative.

12) All materials brought at site shall be got approved from the Engineer-in-charge before being used. The Contractor shall, at his expense and without delay supply for approval to engineer-in-charge, samples of each material such as square bar, flat bar, MS flat & MS Tee, MS angle and other items along with test certificate as desired.

13) Contractor shall carry out the various tests as enumerated in CPWD/BIS specification.

14) The welding, if involved, must be thoroughly joined & beads; kinks should not be visible. The jointing flux material should be uniformly spread to achieve desired strength. Grinder shall be used to remove bulged out metallic flux.

15) No sub-Contracting or sub-letting is allowed.

16) Quantities shown in the schedule are tentative and may change as per site conditions.

17) 10% ± deviation in quantities would be permitted.

18) Quantities are indicative and likely to vary. Bidder will have no objection for variation in quantities thereon. Payment will be as per actual work executed.

19) The lowest bidder will be awarded order for work.

20) The Director, ICGEB reserves the right to cancel any or all the tenders without assigning any reason.

21) Duly sealed tender shall be dropped in the tender box placed at the reception counter of the ICGEB building.

22) No escalation in any form either of materials or of labor shall be payable by the Centre.

23) No T & P and scaffolding shall be supplied by the Institute.

24) No advance payment shall be made except if specified otherwise in the tender.

25) **Performance Guarantee @5%** shall be deposited to the department on the tendered amount by the agency before award of work. S.D. @5% will be with held while releasing of payment & same will be refunded after expiry of warranty/defect liability period for minimum one year or as per T&C of OMC.

26) Security **deposit of 5%** of bill amount will be deducted and same will be released after successful expiry of defect liability of 12 months from date of completion of Work. EMD amount of success bidder will be adjusted against Performance Guarantee/Security Deposit.

27) EMD of unsuccessful bidders will be returned after finalization of tender.

28) EMD is liable to be forfeited if the contractor fails to commence the work as per award letter.

29) For proper completion of the work, if any quantity variation or extra items are required, the bidder shall execute the same. Rates of extra items shall be derived from the tender itself as far as possible or else prevailing market rates shall be adopted.

30) In case the bidder resiles from the offer within the validity of tender or contractor fails to work as per specification after issue of the award letter, the earnest money will be forfeited. Other suitable administrative punitive action may also have imposed as deemed fit.

31) Time allowed for the work shall be strictly followed otherwise the Contractor shall be liable to pay compensation at the rate of 1 % of the contract value of the job undone per week of delay on the part of the Contractor subject to a maximum of 10% of the total contract value.

32) For site visit and any further clarifications, you may visit ICGEB on any working day (Monday to Friday) between 9.30 a.m. to 5 p.m. (contact person Mr.Naresh Chand Dabral Mr Joby John).

33). Payment terms: No advance is permissible under normal circumstance. Bill of the full work may be submitted after satisfactory installation & completion of work (within 15 days of completion).

 However, for any reason beyond the control of the Contractor the extension of time shall be granted upon application by the Contractor in prescribed format. No claim for any compensation during the extended period shall be entertained and the ICGEB’s decision in this regard shall be final.

**FINANCIAL BID**

|  |  |  |  |
| --- | --- | --- | --- |
| **S. No.** | **Item Description** | **Qty** | **Amount** |
|  |  |  | **Each** | **Total** |
| 1 | Supply,installation,testing and commissioning of 16700 CFM at 50mm wc factory fabricated double skin chilled water air handling unit horizontal type (floor model)fabricated out of extruded aluminium section with 0.6 mm preplasticized / pre coated galvanized steel sheet outside & 0.6 mm plain galvanized steel sheet inside with DIDW forward curved blower, blower section and blower motor TEFC type suitable for operation on 415 volts +- 10 %, 50 Hz +- 5 % AC supply , 6 Row deep chilled water cooling coil made of Aluminium finned copper tube (tube thickness 0.5mm) with coil section, pre filter section with non woven synthetic media of 10 micron particle size with an efficiency of 90 %, polished stainless steel drain pan made out of at least 20 G thick sheet duly insulated, complete with motor and belt drive package etc. The AHU panels shall be insulated with 23 mm thick & 38 kg/cum density PU foam. The complete AHU shall conform to standard specifications. The face velocity across cooling coil shall be limited to 150 MPM max. The capacity of Air Handling unit shall be as mentioned hereunder. (MAKE ZECO/EDGETECH/WAVES/) |   |  |  |
| a | 16700 CFM at 50 mm WC, | 1 |  |  |
| b | 10700 CFM at 50 mm WC | 1 |  |  |
| c | 8700 CFM at 50 mm WC, | 2nos |  |  |
| d | 5700 CFM at 50 mm WC | 2 nos |  |  |
| 2 | Supply,installation,testing and commissioning of 6000 CFM at 50mm wc factory fabricated double skin chilled water air handling unit horizontal type (floor model)fabricated out of extruded aluminium section with 0.6 mm preplasticized / pre coated galvanized steel sheet outside & 0.6 mm plain galvanized steel sheet inside with DIDW forward curved blower, blower section and blower motor TEFC type suitable for operation on 415 volts +- 10 %, 50 Hz +- 5 % AC supply , 8 Row deep chilled water cooling coil made of Aluminium finned copper tube (tube thickness 0.5mm) with coil section, pre filter section with non woven synthetic media of 10 micron particle size with an efficiency of 90 %, polished stainless steel drain pan made out of at least 20 G thick sheet duly insulated, complete with motor and belt drive package etc. The AHU panels shall be insulated with 23 mm thick & 38 kg/cum density PU foam. The complete AHU shall conform to standard specifications. The face velocity across cooling coil shall be limited to 150 MPM max. The capacity of Air Handling unit shall be as mentioned hereunder. (MAKE ZECO/EDGETECH/WAVES/) | 01 no |  |  |
| 3 | Providing and fixing butterfly valves of following size duly insulated complete as required. (Make: Audco/ Honeywell/Advance) |   |  |  |
| a | 80mm  | 2 nos |  |  |
| b | 65 mm  | 06 nos |  |  |
| 4 | Supply ,installation,testing and commissioning of Y type pipeline strainers of following size duly insulated and necessary fittings complete as required(make;Advance,Zoloto) . |  |  |  |
| a | 80 mm | 01 nos |  |  |
| b | 65 mm | 05 nos |  |  |
| 5 | Providing and fixing balancing valves of following size duly insulated complete as reqd.(make;Advance/sant/zoloto) |   |  |  |
| a | 80mm  | 1 |  |  |
| b | 50 mm  | 5 nos |  |  |
| 6 | Supply ,installation,testing and commissioning of 65 mm size c class MS pipe with insulation with necessary fittings and insulating chilled pipeline using "TF" grade expanded polystyrene moulded pipe sections of density not less than 20kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) covered with a layer of 120 grams/sq m polythene sheet (vapour barrier) & finally applying 0.63mm Aluminium sheet cladding complete as required. ( Pipe make JINDAL,TATA / EPS insulation make: Beardsell ) | 30 meter |  |  |
| 7 | Supply, installation, testing & commissioning of 2 way modulating valve, linier type,thermostat,temperature controller, interconnecting wires,flange,nut,bolt,welding complete as required (Make, SIEMENS,DANFOSS). The size of modulating valve shall be as mentioned hereunder.  |   |  |  |
| a | 65 mm  | 02 nos |  |  |
| b | 50 mm  | 19 nos |  |  |
| c | 32 mm | 10 nos |  |  |
| 8 |  Supply ,installation,testing and commissioning of duct connect new AHU to existing ducting used 22 gauge GSS in class v111,as per IS 655 and,thermal insulation of supply air duct with crosslinked closed cell performed section of polyethylene(FR)insulation of 13 mmthick laminated with aluminium matalised polyester foil .  | 20 sq met |  |  |
| 9 | Supply, installation, testing and commissioning of Mercury filled **'V' form thermometer** with SS/browns body, thermo well as required(Make H GURU,JASPIN ). | 14 nos |  |  |
| 10 | Providing and fixing of pressure gauge 0-10 kg/sq cm,100 mm dial size,with ss syphon,heavy duty isolating ball valves ,1/2 inch ball valve for AHU water air purging complete as required.(Make H GURU,JASPIN ).). | 14 nos |  |  |
| 11 | Providing and fixing good quality fire retardent flexible canvass connections complete as required | 07 nos |  |  |
| 12 | Modification of ducting arrangement near AO's room to block the existing duct connection from the existing AHU (this AHU 2000 cfm presently installed in the AO's secretariate room shall be dismantled and removed permanently, AHU room separation two side 04 inch brick wall removing repairing and painting as required ) and to connect the main duct running in the corridor with the existing ducting to feed the AO's room as required. | 01 job |  |  |
| 13 |  Buy back of dismantled AHU materials. | 07 nos |  |  |

|  |  |
| --- | --- |
| Total Cost (including 07 nos AHU buy back) |  |